## Tutorial
Scroll Down --> Additional Steps
STEP 1
Enter the following setpoints:
1)No-Flow Speed
2)Rated Speed
3)No-Flow Pressure
4)Rated Pressure
STEP 2
Leave the Curve Approximation initially set to 50%. This is a good starting point.
STEP 5
Click CALCULATE to generate the Calculated System Curve based on the entered Curve Approximation.
The Calculated System curve & corresponding calculated values will now be displayed.
Indicates the Curve Approximation needs to be decreased.
Indicates the Curve Approximation needs to be increased.
STEP 6
Adjust the Curve Approximation (& press CALCULATE) until the Calculated System curve matches the Actual. This may take several attempts.
Use the indicators to help adjust the Curve Approximation.
STEP 7
Once the Calculated System curve matches the Actual, record the final Curve Approximation.
The Actual System curve will now be displayed.
STEP 4
At each setpoint, allow the pressure to reach steady state. Record the corresponding pressure feedback.
STEP 3
Manually operate the pump at various sequential setpoints between No-Flow Speed & Rated Speed. Enter at least 10 setpoints (max 25).

## Terms & Definitions
Terms & Definitions
No-Flow Speed | The speed of the motor at which flow has effectively stopped and minimum or no-flow pressure is achieved.
Rated Speed | Maximum or highest speed that the pump will operate at.
No-Flow Pressure | The minimum or no-flow pressure corresponding to no-flow speed.
Rated Pressure | The pressure produced at the maximum speed of the pump.
Curve Approximation | Adjusts the shape of the calculated system curve. Needs be adjusted such that the calculated system curve matches or overlays the actual system curve. 0% = Linear, 100% = Ideal (or x2)

## Data
No-Flow Speed | 0 | Hz
Rated Speed | 60 | Hz
No-Flow Pressure | 0 | 'P' units
Rated Pressure | 100 | 'P' units
Curve Approximation | 50 | % |  | -0.0044457
Speed Setpoint | Pump Speed Hz | Actual Pressure Feedback 'P' units | Calc System Curve 'P' units
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15 |  |  |  | 0
16 |  |  |  | 0.067589
17 |  |  |  | 0.24132
18 |  |  |  | 0.13648
19 |  |  |  | 0.12328
20 |  |  |  | 0.087162
21 |  |  |  | 0.091568
22 |  |  |  | -0.11148
23 |  |  |  | -0.23567
24 |  |  |  | -0.2719
25 |  |  |  | -0.18169
26 |  |  |  | 0
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50